BILCO Type SS-50SVTB thermally broken automatic smoke vents aid Firefighters in bringing a fire under control by removing smoke, heat and gases from a burning building. Smoke vents feature a frame and cover design that minimizes heat transfer between interior and exterior metal surfaces.  The result is a product that resists harmful condensation and provides superior energy efficiency.  Type SS-50SVTB thermally broken smoke vents are ideal for applications requiring smaller vent areas, such as elevator shafts or stair wells. Units are available in aluminum construction. For more information, please visit our website www.bilco.com or call 1-800-366-6530.

SECTION 077236

AUTOMATIC SMOKE VENTS

(BILCO TYPE SS-50SVTB)

- GENERAL

      - SUMMARY

        - Work Included:  Provide factory-fabricated single-leaf automatic smoke vents.

      - SUBMITTALS

        - Product Data:  Submit manufacturer’s product data.

        - Shop Drawings: Submit shop drawings including profiles, accessories, location, fusible links, adjacent construction interface, and dimensions.

        - Warranty:  Submit executed copy of manufacturer’s standard warranty.

      - QUALITY ASSURANCE

        - Manufacturer:  A minimum of 5 years experience manufacturing similar products.

        - Installer:  A minimum of 2 years experience installing similar products.

        - Manufacturer’s Quality System: Registered to ISO 9001 Quality Standards including in-house engineering for product design activities.

      - DELIVERY, STORAGE AND HANDLING

        - Deliver products in manufacturer’s original packaging.  Store materials in a dry, protected, well-vented area. Inspect product upon receipt and report damaged material immediately to delivering carrier and note such damage on the carrier’s freight bill of lading.

      - WARRANTY

        - Manufacturer’s Warranty:  Provide manufacturer’s standard warranty. Materials shall be free of defects in material and workmanship for a period of five years from the date of purchase. Should a part fail to function in normal use within this period, manufacturer shall furnish a new part at no charge.

- PRODUCTS

      - manufacturer

        - Basis-of-Design Manufacturer: Type SS-50SVTB Automatic Roof Smoke Vent by The BILCO Company, P.O. Box 1203, New Haven, CT 06505, 1-800-366-6530, Fax: 1-203-535-1582, Web: www.bilco.com.

      - AUTOMATIC ROOF FIRE VENT

        - Furnish and install where indicated on plans metal fire vent Type SS-50SVTB. size [insert: width (______) x length (______)]. Length denotes hinge side. The roof fire vent shall be single leaf and preassembled from the manufacturer.

        - Performance characteristics:

          - Vent(s) shall be UL listed.

          - Cover and curb shall be thermally broken to prevent heat transfer between interior and exterior surfaces.

          - Cover shall be reinforced to support a minimum live load of 40 psf (195kg/m2) with a maximum deflection of 1/150th of the span and 90 psf (438kg/m2) wind uplift.

          - Lifting mechanism assemblies shall open the vent cover when latch is manually released or when heat breaks the UL listed fusible link. Opening shall be in a controlled manner to avoid damage to surrounding roof surfaces.

          - Entire roof fire vent shall be weather tight with fully welded corner joints on cover and curb.

          - Latch mechanisms shall hold the covers in the closed position without overstressing the fusible link and withstand 90 psf (438kg/m2) wind uplift forces acting on the cover.

          - Latch operation: When heat parts the UL listed fusible link, the latch shall release instantaneously, allowing vent cover to open. The latch shall be designed for easy resetting, after a fire or test, so that the cover cannot be latched closed unless the mechanism has been reset properly. Manufacturer shall provide instructions for resetting the latch with each unit.

        - Cover: Shall be 11-gauge (2.3mm) aluminum with a 5” (127mm) beaded flange with formed reinforcing members. Interior and exterior surfaces shall be thermally broken to minimize heat transfer and to resist condensation. Cover shall have a heavy extruded EPDM rubber gasket bonded to the cover interior to assure a continuous seal when compressed to the top surface of the curb.

        - Cover insulation: Shall be 3” (75mm) thick polyisocyanurate with an R-value = 20.3 ft2hrF/BTU [U-Value = 0.049 BTU/ft2hrF], fully covered and protected by an 18-gauge (1mm) aluminum liner.

        - Curb: Shall be 12” (305mm) in height and of 11-gauge (2.3mm) aluminum. Interior and exterior surfaces shall be thermally broken to minimize heat transfer and to resist condensation. The curb shall be formed with a 5-1/2” (140mm) flange with 7/16” (11mm) holes provided for securing to the roof deck. The curb shall be equipped with an integral metal capflashing of the same gauge and material as the curb, fully welded at the corners, that features the Bil-Clip® flashing system, including stamped tabs, 6” (153mm) on center, to be bent inward to hold single ply roofing membrane securely in place.

        - Curb insulation: Shall be 3” (75mm) thick polyisocyanurate with an R-value = 20.3 ft2hrF/BTU [U-Value = 0.049 BTU/ft2hrF].

        - Lifting mechanisms: Corrosion resistant gas springs open covers automatically against a 10 lb./ft2 (49Kg/m2) snow/wind load. Gas springs shall have built in dampers to assure a controlled rate of opening and automatically lock the cover in the fully open position. A release mechanism shall be provided to allow the covers to be closed.

        - Latch mechanism: Shall be the BILCO Thermolatch® positive hold/release mechanism controlled by a single UL listed fusible link. Fusible link shall be curb mounted on a non-hinged end to allow the latching mechanism to be easily reset from the roof level.

        - Hardware

          - Heavy stainless steel pintle hinges shall be provided.

          - Cover shall automatically lock in the open position with a rigid hold open arm equipped with a 1” (25mm) diameter red vinyl grip handle to permit easy release for closing.

          - Corrosion resistant gas springs and hot dip galvanized steel stop cables. All other hardware is zinc plated/chromate sealed.

          - Cover hardware shall be bolted into heavy gauge channel reinforcing welded to the underside of the cover and concealed within the insulation space.

          - Gas springs shall have built in dampers to assure a controlled rate of opening and automatically lock the cover in the fully open position.

        - Manual pull release cables: Interior and exterior cables with red vinyl grips shall be provided and allow the unit to be opened without disturbing the fusible link.

        - Finishes: Factory finish shall be mill finish aluminum.

      - Performance

        - The entire hatch product (not layer sections) shall have a “Developed Area” U-Value of not greater than 0.245 BTU/(ft2hrF) [1.39 W/m2K]. *

        - Both the cover and curb layers shall have a “Homogeneous Section” U-Value of not greater than 0.049 BTU/(ft2hrF) [0.278 W/m2K]. **

- * “Developed Area” U-Value is based on a vent size of 2’-3.5” x 2’-11.44” (900mm x 700mm).

- ** “Homogeneous Section” U-Value is based on a vent size of 3’-0” x 2’-6” (914mm x 762mm).

- EXECUTION

      - EXAMINATION

        - Examine substrates and openings for compliance with requirements for installation tolerances and other conditions affecting performance.  Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - Install products in strict accordance with manufacturer’s instructions and approved submittals.  Locate units level, plumb, and in proper alignment with adjacent work.

          - Test units for proper function and adjust until proper operation is achieved.

          - Test fusible link and install replacement fusible link after testing.

          - Repair finishes damaged during installation.

          - Restore finishes so no evidence remains of corrective work.

      - ADJUSTING AND CLEANING

        - Clean exposed surfaces using methods acceptable to the manufacturer which will not damage finish.

END OF SECTION